ANDD AI NATIVE DISTRIBUTED DATACENTERS A Technical Architecture for Sovereign, Resilient, AI-Managed Edge Infrastructure Whitepaper v2.0 • March 2026 contact@andd.network • andd.network

Table of Contents

01	Executive Summary

02	The Case for Decentralization

03	ANDD Architecture Overview

04	Technical Architecture

05	Bandwidth & Connectivity

06	Energy & Mitigation Strategies

07	AI-Native Operations

08	Resilience Through Decentralization

09	Payment Architecture

10	DePIN Integration & Pressure Test

11	Opportunity Zone Alignment

12	Implementation Roadmap

13	Conclusion

01  Executive Summary

The global compute infrastructure serving AI, critical services, and digital economies is dangerously concentrated. Fewer than 30 hyperscale campuses process the vast majority of U.S. AI inference, financial transactions, government data, and emergency communications.

This concentration creates single points of failure for national security, economic continuity, and community resilience — and leaves underserved regions permanently behind.

The ANDD Model A network of hundreds to thousands of sub-2MW edge datacenters, deployed across Opportunity Zones, forming an interconnected mesh fabric entirely managed by AI. Autonomous onboarding, billing, provisioning, and maintenance — no human operators required for standard operations.

| <2MW | 100s+ | 4 | 99.99% |
| --- | --- | --- | --- |
| Per Site | Locations | HW Domains | SLA Target |

Enterprise-grade edge infrastructure

This whitepaper details the four hardware domains, bandwidth and energy profiles, AI-native operations model, payment architecture spanning fiat to crypto micro-transactions, and a rigorous pressure test against existing DePIN projects.

02  The Case for Decentralization

The Concentration Problem

Northern Virginia hosts over 70% of East Coast internet traffic. The top five metro markets account for the majority of U.S. datacenter capacity. This creates compounding vulnerabilities:

• National Security. A coordinated attack on fewer than a dozen campuses could degrade federal agencies, financial markets, and defense communications simultaneously.

• Latency Inequality. Communities >50ms from hyperscale regions cannot access real-time AI, telemedicine, or autonomous vehicle coordination.

• Sovereignty Erosion. Government data depends on three to four hyperscale vendors' operational decisions and pricing.

• Grid Strain. A single 300MW campus demands the output of a small power plant, straining regional grids.

Concentrated infrastructure leaves most communities behind

Why Now

• AI Inference at the Edge. 60–70% of all AI compute is inference — latency-sensitive, geographically distributed, ideal for edge.

• DePIN Needs Upgrading. Consumer hardware hits reliability ceilings. Enterprise customers need 99.99% uptime and compliance.

• Federal Policy Tailwind. Opportunity Zones (8,764 tracts), bipartisan AI infrastructure support, rural broadband funding.

The AI-Native Unlock

Previous distributed datacenter attempts failed on economics — sub-2MW sites can’t justify full operations teams. ANDD inverts this: AI handles onboarding, provisioning, billing, monitoring, and maintenance. The marginal cost of a new site approaches hardware cost alone.

03  Architecture Overview

Interconnected mesh fabric — no single point of failure

Three-Tier Mesh Fabric

| Tier | Component | Power | Role |
| --- | --- | --- | --- |
| 3 | AI Control Plane | Distributed | Global routing, billing, capacity planning |
| 2 | Regional Hubs | 1–2MW | Aggregation, peering, training GPUs |
| 1 | Edge Nodes | 200kW–500kW | Local compute, inference, storage |

Connectivity Per Node

| Link Type | Medium | Bandwidth |
| --- | --- | --- |
| Primary uplink | Fiber / microwave | 10+ Gbps |
| Redundant uplink | Diverse fiber / 5G / LEO sat | 1–10 Gbps |
| Mesh peering | Direct node-to-node | 10 Gbps |
| 2nd hub path | Via mesh or direct | Variable |

Site Layout

| System | Components | Spec |
| --- | --- | --- |
| IT | Compute (x4–8) + AI (x2–4) + Storage (x2–4) | Configurable mix |
| Network | Leaf-spine + edge router | 100/400GbE + BGP |
| Power | Utility + ATS + UPS + solar/BESS | Microgrid capable |
| Cooling | DLC + immersion + air economizer | PUE 1.15–1.25 |

04  Technical Architecture

AI Accelerators

Purpose-built silicon for edge inference

| Accelerator | TDP | Memory | Tier |
| --- | --- | --- | --- |
| NVIDIA L4 | 72W | 24GB | Edge (efficient) |
| NVIDIA L40S | 300W | 48GB | Edge (inference) |
| AMD MI300X | 750W | 192GB HBM3 | Edge / Hub |
| AMD MI325X | 750W | 256GB HBM3e | Edge / Hub |
| Intel Gaudi 3 | ~600W | 128GB HBM2e | Edge (cost) |
| NVIDIA H100 | 700W | 80GB HBM3 | Hub (train) |
| NVIDIA H200 | 700W | 141GB HBM3e | Hub (large) |
| NVIDIA B200 | 1,000W | 192GB HBM3e | Hub (train) |
| GB200 NVL2 | 2,700W | 384GB HBM3e | Hub (liquid) |

Edge AI Feasibility

| Workload | Hardware | Power | Latency |
| --- | --- | --- | --- |
| LLM 7–13B | 1x L40S | 300W | 20–100ms/tok |
| LLM 70B | 2–4x H100 | 700W–1.4kW | 50–200ms/tok |
| Image/video | 1x L4 | 72W | 5–20ms |
| Speech | 1x L4 | 72W | <100ms |
| RAG pipeline | 1–2x H100 | 1–2kW | 100–500ms |
| Fraud detection | 1x L40S | 300W | <50ms |

Software Stack

| Layer | Components |
| --- | --- |
| AI Management | Onboarding, Provisioning, Billing, SLA agents |
| Orchestration | K3s/RKE2, Istio mesh, AI scheduler |
| Infrastructure | SDN (OVS/VPP), Ceph/MinIO, AI-controlled DCIM |
| Hardware | BMC/Redfish, GPU drivers, SONiC/Cumulus |

Security

• Zero-trust: mTLS on all workload-to-workload communication

• Hardware root of trust: TPM 2.0, measured boot, remote attestation

• Tenant isolation: SR-IOV, SEV-SNP/TDX confidential compute

• Physical: Biometric access, AI surveillance, SCIF options

• Compliance: FedRAMP, SOC 2, HIPAA, CJIS, ITAR

05  Bandwidth & Connectivity

| Tier | Primary | Redundant | Mesh | Total |
| --- | --- | --- | --- | --- |
| Edge 200kW | 10G | 1–10G | 10G | 20–30G |
| Edge 500kW | 40G | 10G | 25G | 50–75G |
| Hub 1–2MW | 100G | 40G | 100G | 200–300G |

Redundant, multi-path connectivity

Backhaul by Geography

| Type | Primary | Backup |
| --- | --- | --- |
| Urban | Multi-carrier fiber 10–40G | 5G/LTE 1–5G |
| Suburban | Fiber 10–40G | Diverse fiber 10G |
| Rural | Licensed wireless / LEO sat 1–10G | 5G/LTE |

Protocol Stack

• Underlay: eBPF + SRv6 segment routing

• Overlay: WireGuard/MACsec + VXLAN/GENEVE

• Peering: Automated BGP with RPKI

• DNS: Anycast across all nodes

• GSLB: AI-driven, latency/cost/carbon aware

06  Energy & Mitigation

| Tier | IT | Cooling | Infra | Total | PUE |
| --- | --- | --- | --- | --- | --- |
| Edge 200kW | 150kW | 25kW | 25kW | 200kW | 1.15–1.25 |
| Edge 500kW | 380kW | 65kW | 55kW | 500kW | 1.15–1.25 |
| Hub 2MW | 1,500kW | 280kW | 220kW | 2MW | 1.15–1.25 |

Cooling Comparison

| Technology | Cooling kW | IT Capacity | PUE |
| --- | --- | --- | --- |
| Air (DX) | 150–200kW | 300–350kW | 1.40–1.80 |
| Rear-door HX | 75–125kW | 375–425kW | 1.20–1.40 |
| Direct liquid | 40–75kW | 425–460kW | 1.10–1.20 |
| Immersion (1φ) | 15–30kW | 470–485kW | 1.02–1.06 |
| Immersion (2φ) | 10–20kW | 480–490kW | 1.01–1.04 |

30% More Compute, Same Power Moving from air cooling to immersion saves ~300kW per MW — increasing usable compute by 30% within the same power envelope.

Renewable Economics

| Component | Spec | Cost | Value |
| --- | --- | --- | --- |
| Solar | 100kW carport | ~$150K | 175 MWh/yr |
| BESS (LFP) | 500kWh/250kW | ~$200K | 2hr backup + cycling |
| IRA ITC | 30–50% | –$105K–$175K | Capital reduction |
| Grid services | Freq. reg + DR | — | $50–200K/yr/MW |

Effective payback: 2–4 years after incentives.

Federal Funding

| Program | Amount | Use |
| --- | --- | --- |
| DOE GRIP | $10.5B | Microgrids, DER |
| DOE LPO | $400B+ | Clean energy lending |
| ARPA-E COOLERCHIPS | $42M | DC cooling R&D |
| IRA ITC | 30–50% | Solar, BESS, fuel cells |
| NTIA BEAD | $42.45B | Broadband + edge |

07  AI-Native Operations

AI agents manage the entire datacenter lifecycle

Traditional operations require full-time staff per site, establishing a ~5MW minimum viable size. ANDD eliminates this with autonomous AI agents:

| Agent | Function |
| --- | --- |
| Orchestration | Coordinates sub-agents, escalates exceptions |
| Onboarding | Lead qualification, proposals, KYC, provisioning |
| Provisioning | Workload mapping, node placement, auto-scaling |
| Billing | Sub-second metering, invoicing, fiat+crypto reconciliation |
| Maintenance | Sensor telemetry, digital twins, preventive scheduling |
| SLA Guardian | Threshold monitoring, auto-remediation, credit issuance |

1 Human per 20–50 Nodes A 10–25x improvement over traditional staffing. Humans handle exceptions, strategy, physical maintenance, and compliance oversight.

Self-Hosting Architecture

• Foundation LLM runs on ANDD’s own GPUs — no external API dependency

• Specialized models for maintenance, networking, billing

• Staged rollout: shadow → canary → full, with auto-rollback

• Full reasoning chain logging for auditability

08  Resilience Through Decentralization

Distributed architecture eliminates single points of failure

Payments

Distributed card authorization, ACH, FedNow gateways across hundreds of nodes. Local store-and-forward during backbone disruptions. Crypto rails as backup settlement layer.

Energy Grid

Distributed SCADA/EMS hosting. Edge compute for DER control loops (<10ms). Virtual power plant from distributed BESS. Microgrid islanding during emergencies.

Emergency Services

Local NG911 hosting. FirstNet edge compute. Emergency operations center computing. LEO satellite backhaul when terrestrial networks fail.

Utilities & Water

Local SCADA for water/wastewater/gas. Semi-air-gapped operation. AI anomaly detection for contamination and cyber intrusion.

Quantified Advantage

| Architecture | Per-Unit Uptime | System Availability |
| --- | --- | --- |
| Single hyperscale | 99.99% | 99.99% (67 min/yr down) |
| ANDD mesh (100 nodes) | 99.95% per node | 99.9999%+ (graceful degradation) |

09  Payment Architecture

Fiat Tiers

| Tier | Model | Methods | Use Case |
| --- | --- | --- | --- |
| Starter | Monthly | Card, ACH | Startups |
| Professional | Monthly/Annual | ACH, wire | Mid-market |
| Enterprise | Annual | Wire, PO | Large enterprise |
| Government | Multi-year | Treasury/PO | Federal/state/local |

Crypto & Micro-Transactions

| Rail | Use Case | Finality | Cost/Tx |
| --- | --- | --- | --- |
| Ethereum L1 | Enterprise contracts | ~12 min | $1–$20 |
| Solana | High-frequency | Sub-second | ~$0.001 |
| L2 (Arbitrum/Base) | Medium-frequency | Minutes | $0.01–0.10 |
| Payment channels | Micro-transactions | Instant | Near-zero |

Smart Contract SLAs

Programmable SLAs encode uptime targets, latency floors, and measurement periods. Oracle-fed performance data triggers automatic stablecoin credit issuance on breach — no human claims process.

Hybrid Orchestration

| Customer | Primary | Secondary | Micro-Tx |
| --- | --- | --- | --- |
| Enterprise | Wire/ACH | Card | N/A |
| Government | PO/Treasury | ACH | N/A |
| Startup | Card | USDC | Per-API |
| DePIN | Stablecoin | Payment channel | Per-request |
| Web3 | USDC/token | Payment channel | Per-request |

10  DePIN Pressure Test

Enterprise-grade backbone for decentralized protocols

Lessons from DePIN Projects

| Project | Success | Failure | ANDD Fix |
| --- | --- | --- | --- |
| Helium | 900K+ hotspots | No SLA, wrong locations | AI-driven demand placement |
| Filecoin | 22+ EiB capacity | Empty capacity, slow retrieval | Utilization-based incentives |
| Render | Real 3D rendering demand | Consumer GPUs can’t do AI | Datacenter-grade GPUs |
| Akash | 70–85% cheaper | No SLA enforcement | Smart contract SLAs |
| io.net | GPU clustering for ML | Heterogeneous, high latency | Homogeneous co-located HW |

The Enterprise-Grade Gap

| Dimension | Consumer DePIN | ANDD |
| --- | --- | --- |
| Uptime | 90–98% | 99.99% SLA-backed |
| Redundancy | None | N+1 power/cooling/network |
| Security | None | Biometric, surveillance |
| Compliance | None | FedRAMP, SOC 2, HIPAA |
| Power | Residential | UPS + BESS + fuel cell |
| Cooling | Consumer fans | DLC + immersion |
| Connectivity | Broadband | Multi-provider, SLA |
| Sovereignty | Unknown | Per-tenant geo-restrictions |

ANDD Completes DePIN The tokenomics and demand aggregation work. The physical infrastructure needs upgrading to enterprise grade. ANDD provides that backbone.

What Can Be Built on ANDD

| Category | Examples | Why Edge Required |
| --- | --- | --- |
| Smart City / IoT | Traffic, sensors, digital twins | <10ms control loops |
| Autonomous Vehicles | V2X, HD maps, inference | Safety-critical latency |
| Health AI | Diagnostics, monitoring | HIPAA + low latency |
| Edge AI / MLOps | Model serving, RAG, agents | GPU at the edge |
| DePIN Protocols | Compute, storage, wireless | Enterprise backbone |
| Fintech | Payments, fraud detection | Compliance + <50ms |
| Content Delivery | Video, gaming, AR/VR | Bandwidth offload |
| Defense | Classified, SIGINT, C2 | Sovereign infrastructure |
| Emergency Services | NG911, FirstNet, alerts | Functions during disasters |
| AgTech | Precision ag, drones | Rural edge compute |

11  Opportunity Zone Alignment

| Tier | Incentive | Requirement | Benefit |
| --- | --- | --- | --- |
| 1 | Capital gains deferral | Invest in QOF | Defer tax; rolling 5-yr window |
| 2 | Basis step-up | Hold 5+ years | 10% (30% rural) |
| 3 | 10-year exclusion | Hold 10+ years | Zero tax on appreciation |

Community Impact (200kW Node)

| Impact | Estimate |
| --- | --- |
| Construction jobs | 15–30 (6–12 month build) |
| Permanent jobs | 1–3 technicians |
| Property tax | $50K–$150K/yr |
| Utility revenue | $150K–$300K/yr |
| Multiplier | 1.5–2.0x direct spending |
| Digital benefit | Gigabit + AI + edge compute |

12  Implementation Roadmap

| Phase | Timeline | Milestones |
| --- | --- | --- |
| Foundation | Mo 1–12 | AI layer, 200kW design, 3–5 pilots, SOC 2, QOF |
| Formation | Mo 12–24 | 20–50 nodes, hubs, >90% autonomous, FedRAMP |
| Scale | Mo 24–48 | 100–300 nodes, smart SLAs, federal customers |
| Continental | Mo 48–72 | 500–1000+ nodes, full autonomy, VPP |

13  Conclusion

The concentration of compute into hyperscale campuses was an artifact of an era when operational economics demanded scale and AI didn’t exist as an operational tool. That era is ending.

ANDD demonstrates that AI-native operations eliminate the economic barrier to distributed deployment. The marginal cost of a new edge node approaches hardware cost alone.

ANDD delivers: • Sovereignty — compute stays where it’s governed • Security — no single target degrades the network • Resilience — survives what cripples centralized • Equity — capabilities reach underserved communities • DePIN — enterprise backbone for decentralized protocols • Viability — fiat to crypto, subscriptions to micro-tx

The question is how quickly it can be deployed.
ANDD is the answer.

contact@andd.network  •  andd.network

This document contains forward-looking statements. Technical specifications represent design targets. Tax information is for informational purposes only.